## Slide 1
WEEK 8 · PROJECTS + DESIGN
Final Projects & Data Center Design
Choose a capstone · analyze one small facility together
CYBER 444 · Systems & Network Administration
October 20 & 22, 2026
Notes: Launch the final projects first, retaining the published end-of-Week-9 proposal deadline. Then introduce the fictional two-rack facility for board calculations and cover the 18 chapters of the Keentel Engineering guide. Instructor-led activities are done on the board rather than on separate slides. Citations: - /opt/byu-cyber-444.github.io/final-project-cyber/index.md - /opt/byu-cyber-444.github.io/final-project-it/index.md - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide - /opt/byu-cyber-444.github.io/schedule/week-08.md

## Slide 2
FINAL PROJECT
Choose one capstone; build evidence you can defend
Either track is open to every student, regardless of weekly track.
CHOOSE
One Cyber or IT option
PROPOSE
PDF due end of Week 9
BUILD
Weeks 9–15 in your lab
DEFEND
Docs + recorded demo ≤10 min
Dec 10, 11:59 PM
Course rules
Work alone or in a pair. The project is the final exam; ask staff about scope or grading, not project implementation.
Notes: Launch the project here in Week 8. Both tracks allow individual or pair work with the same scope. The passing proposal is required. Final documentation and a recorded presentation/demo of 10 minutes or less are due December 10 at 11:59 PM in Learning Suite, each worth 5% of the course grade. No graded checkpoints occur between proposal and final submission. Project assistance restrictions are stated on both track overviews. Citations: - /opt/byu-cyber-444.github.io/final-project-cyber/index.md - /opt/byu-cyber-444.github.io/final-project-it/index.md

## Slide 3
CYBER OPTIONS
Six Cyber projects: choose a system to secure
Each option requires meaningful Linux and Windows Server roles.
C1
Hardened infrastructure — CIS Level 2 or DISA STIG
C2
Zero-trust identity and PKI platform
C3
Detection engineering / SOC-in-a-Box
C4
Compliance-as-Code pipeline
C5
Secure container platform
C6
Patch and vulnerability management program
Notes: Ask students to identify which option best uses the skills and infrastructure they already have. The Cyber overview lists all six options. Every Cyber project includes at least one Linux system and one Windows Server system doing real work; both appear in automation, diagram, documentation, and demo. Citations: - /opt/byu-cyber-444.github.io/final-project-cyber/index.md

## Slide 4
IT OPTIONS
Five IT projects: choose an operations problem
All IT options run in the student’s own Proxmox environment.
I1
HA platform with backup and disaster recovery
I2
Monitoring and service desk
I3
On-prem AI inference service
I4
Identity and endpoint lifecycle
I5
Self-service provisioning and golden images
Selection lens
Which option fits your available RAM, time, and evidence you can capture?
Notes: Invite students to compare operational value, resource load, and evidence burden. The IT overview says these projects can run in the student’s own Proxmox lab; no cloud account is required. Most options use Valley Medical Group as the scenario organization. Citations: - /opt/byu-cyber-444.github.io/final-project-it/index.md

## Slide 5
PROPOSAL
A passing proposal makes the build concrete
Submit one PDF in Learning Suite by the end of Week 9.
Option + team
Name the option; pairs identify each person’s ownership
Scope
Answer every checklist item on the chosen option page
Infrastructure
Hostnames, OS, roles, addresses, RAM, disk, and heaviest service
Tools
Name and justify automation, test/scan, and evidence tools
Milestones
Specific outputs for Weeks 10, 11, 12, and 14
Notes: Both proposal pages require all five sections and specific answers. Week 13 is Thanksgiving break with no deliverable. The Cyber proposal additionally requires at least one Linux and one Windows Server system and the Windows role. A failed proposal must be revised and passed before project credit can be received. Do not imply the Week 8 launch changes the deadline. Citations: - /opt/byu-cyber-444.github.io/final-project-cyber/proposal.md - /opt/byu-cyber-444.github.io/final-project-it/proposal.md

## Slide 6
CLASS SCENARIO
The small data center: starting loads
Use this fictional facility for board calculations and outage tests.
STARTING TOPOLOGY · use for board calculations
UTILITY
25 kW usable
GENERATOR
15 kW
ATS + PANEL
A PATH
UPS 9 kW · PDU 8 kW
B PATH
UPS 9 kW · PDU 8 kW
Dual-powered core + single-cord devices
EQUIPMENT + LOADS
DUAL PSU IT
4 compute 4.0 kW; storage 1.5 kW
A ONLY
switch 0.5 kW; backup NAS 0.8 kW
B ONLY
switch 0.5 kW
COOLING
2 CRACs; each draws 4 kW, removes 8 kW
OTHER
lights / facility 0.7 kW
Board goal
Assess 2.0 kW of added dual-powered IT load and one power-path or cooling-unit outage.
Notes: Baseline measured IT load is 7.3 kW: four compute servers 4.0, shared storage 1.5, switches 0.5 each, and A-only backup NAS 0.8. Utility service has 25 kW usable capacity. Generator is 15 kW. UPS A and B are each 9 kW output, and PDUs A and B each support 8 kW. Two CRACs each draw 4 kW and can remove up to 8 kW of IT heat. Other facility loads are 0.7 kW. Ask students to draw both the electrical and heat paths. Core service is compute plus shared storage plus at least one switch. The NAS is noncritical. The growth target gives 9.3 kW IT load. Use values as exercise assumptions, not equipment specifications. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 7
CHAPTER 1
The data center converts power into heat
Follow energy from the service entrance to IT and then back outdoors.
POWER IN
Utility and generator
CONVERT
Servers do work
HEAT OUT
Cooling rejects heat
Notes: Chapter 1 frames a data center as an energy-conversion building. Nearly all server electrical draw becomes heat. Introduce the single fictional site that students will refine across all 18 activities. Ask students to track IT load and cooling electrical load separately. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 8
CHAPTER 2
Three imperatives: power, cooling, operation
A working data center keeps all three available through planned and unplanned events.
CONTINUOUS POWER
Condition supply and bridge outages
CONTINUOUS COOLING
Remove heat while IT operates
CONTINUOUS OPERATION
Maintain and repair without avoidable downtime
Notes: Chapter 2 organizes design around uninterrupted power, heat removal, and operation through maintenance or failure. Distinguish the service to protect from every noncritical device in the room. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 9
CHAPTER 3
A data center is not an office building
Its load and heat persist around the clock, so operating practices are part of design.
LOAD
IT and cooling run continuously
FAILURE
Power or cooling loss threatens services quickly
OPERATIONS
Access, maintenance, and response need plans
Notes: Chapter 3 contrasts continuous data center loads with occupancy-driven office loads. Bring in the Week 8 course schedule for physical security and maintenance considerations without attributing those topics to the guide. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide - /opt/byu-cyber-444.github.io/schedule/week-08.md

## Slide 10
CHAPTER 4
From grid to fence: utility supply
A service connection has a capacity, route, protection, and approval process.
UTILITY
Available capacity
SERVICE
Meter + switchgear
SITE
Protected distribution
Notes: Chapter 4 follows grid power through the substation to service entrance switchgear. For this small teaching site, use the stated 25 kW usable utility capacity rather than large-campus voltage examples. A connection is a feasibility question, not a guaranteed commodity. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 11
CHAPTER 5
On-site chain: switchgear to rack
Every stage needs a capacity and a way to isolate faults.
PANEL
Protection and branching
UPS
Condition and bridge
PDU
Distribute to racks
IT
Dual or single supply
Notes: Chapter 5 maps the distribution chain. The small exercise omits medium-voltage campus stages but retains the same logic. Label utility/generator and cooling as separate branches; do not draw two independent power paths where the common ATS still exists. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 12
CHAPTER 6
UPS: condition power and bridge outages
A double-conversion UPS keeps the inverter feeding the critical load.
RECTIFIER
AC to DC
BATTERY
Short-duration stored energy
INVERTER
DC to regulated AC
Notes: Chapter 6 describes double-conversion, line-interactive alternatives, and battery choices. For the exercise, both UPS units have 9 kW output capacity. Runtime is unspecified: students must request a vendor discharge curve for their design rather than assuming capacity equals runtime. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 13
CHAPTER 7
Generator: the long outage handoff
UPS bridges the start and transfer; generator capacity must include the chosen cooling load.
UTILITY LOSS
UPS holds IT
START
Generator stabilizes
TRANSFER
ATS feeds panel
RESTORE
UPS returns to input power
Notes: Chapter 7 describes the automatic sequence from utility failure to UPS battery, generator start, transfer, and restoration. The exercise generator is 15 kW. Do not promise successful transfer without the battery runtime, startup time, and protection study. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 14
CHAPTER 8
Power studies prove the paths will work
Capacity, fault current, breaker selectivity, and maintenance safety need engineering.
LOAD FLOW
Check normal and contingency loading
FAULT + COORDINATION
Interrupt and isolate the right branch
ARC FLASH
Understand maintenance hazards
Notes: Chapter 8 lists load flow, short-circuit, protective-device coordination, and arc-flash studies. Students are not licensed to perform these studies from the classroom diagram; they should identify where specialist engineering evidence is needed. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 15
CHAPTER 9
Every IT watt becomes a cooling problem
Airflow must carry rack heat to the cooling equipment without hot-air recirculation.
IT HEAT
Measured IT kW sets sensible heat load
AIR PATH
Cold intake → hot exhaust
LEAKS
Blanking and sealing protect the path
Notes: Chapter 9 covers IT heat conversion, rack blanks, raised-floor delivery, and hot/cold mixing. Explain 1 kW ≈ 3,412 BTU/h as a unit conversion, not a cooling equipment efficiency claim. The exercise racks should be labeled by load and airflow direction. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 16
CHAPTER 10
Containment keeps supply and return apart
Cold-aisle and hot-aisle schemes close the mixing path.
COLD AISLE
Enclose rack fronts and supply air
HOT AISLE
Enclose rack backs and exhaust
SEALING
Doors, panels, and blanks close gaps
Notes: Chapter 10 compares cold-aisle and hot-aisle containment. The source presents hot-aisle containment as stronger for high-density builds, while cold-aisle can be simpler to retrofit. For a small two-rack site, design justification matters more than asserting one universal best choice. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 17
CHAPTER 11
Cooling units can serve room, row, or rack
CRAC creates refrigeration locally; CRAH transfers cooling from chilled water.
CRAC
Self-contained refrigeration circuit
CRAH
Air handler supplied by chilled-water plant
IN-ROW / RACK
Cooling close to concentrated heat
Notes: Chapter 11 distinguishes CRAC and CRAH and deployment scales. The exercise has two existing CRACs, each removing at most 8 kW IT heat while drawing 4 kW electric. Distinguish heat-removal capacity from electrical consumption. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 18
CHAPTER 12
Chilled water moves heat across the facility
A chiller, pumps, and CRAH coils create a shared cooling loop.
CHILLER
Cool the water
PUMP
Deliver to coils
CRAH
Take room heat
RETURN
Warm water back
Notes: Chapter 12 explains the chilled-water loop and layered plant redundancy. Present it as an option for scale, not a requirement for the small exercise. A self-contained CRAC path remains a valid design choice. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 19
CHAPTER 13
Heat must leave the building
Air-cooled, water-cooled, and economizer modes trade electricity, water, and complexity.
AIR-COOLED
Reject outdoors with fans and coils
WATER-COOLED
Evaporation and water treatment
ECONOMIZER
Use favorable outdoor conditions
Notes: Chapter 13 distinguishes ultimate heat-rejection medium from what circulates inside the building. Avoid claiming an economizer will always save a fixed percentage; climate and control sequence matter. Discuss PUE as a measured ratio of facility to IT power. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 20
CHAPTER 14
Liquid cooling addresses concentrated heat
Direct-to-chip and immersion serve densities where air delivery becomes difficult.
DIRECT-TO-CHIP
Cold plates take heat from processors
IMMERSION
Dielectric fluid surrounds hardware
HYBRID
Residual components still need air
Notes: Chapter 14 introduces liquid cooling for dense AI/GPU systems. For this 9.3 kW total small room, students may reject it as unnecessary. Do not generalize a universal kW threshold from the article; rack density, equipment support, and heat route govern. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 21
CHAPTER 15
Redundancy is a whole-system claim
Uptime Institute Tiers describe whole-facility topology and behavior.
TIER I
Basic capacity
TIER II
Redundant capacity components
TIER III
Concurrently maintainable
TIER IV
Fault tolerant
Design language
N+1 and 2N are component patterns; a Tier has no fixed availability “nines” value.
Notes: Chapter 15 discusses N, N+1, 2N, and tiers. Use Uptime Institute primary descriptions for formal Tier claims and avoid the source article’s simplified fixed-nines association. This classroom diagram cannot claim certification. Power and cooling must meet the same stated failure requirement. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide - Uptime Institute Tier Certification, https://uptimeinstitute.com/tier-certification/ - Uptime Institute, 99 Red Flags, https://journal.uptimeinstitute.com/99-red-flags/

## Slide 22
CHAPTER 16
Controls make power and cooling act together
Monitoring, alarms, and automation turn components into an operating system.
BMS
Stage cooling and track environment
EPMS
Watch breakers, UPS, generator, and power
DCIM
Relate facility status to IT/rack load
Notes: Chapter 16 covers BMS, power monitoring, and DCIM integration. The Week 8 schedule also requires environmental monitoring and out-of-band hardware management. Keep OOB on a dedicated management network with controlled identity; do not place it on the production application VLAN. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide - /opt/byu-cyber-444.github.io/schedule/week-08.md - /opt/byu-cyber-444.github.io/labs/copies/it-lab-08.md

## Slide 23
CHAPTER 17
Site viability precedes equipment choice
Grid capacity and an achievable energization path limit the design envelope.
CAPACITY
Usable utility service and margin
TIMING
Upgrade or connection lead time
GROWTH
Phased load plan
Notes: Chapter 17 focuses on large-load interconnection. Adapt its principle to this small site: confirm the existing 25 kW usable service and future operating draw, not a transmission queue. Keep large-campus process as context in notes rather than a task for students to perform. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide

## Slide 24
CHAPTER 18
Integrate the power and cooling design
One load figure must agree across UPS, distribution, generator, cooling, and site service.
IT LOAD
Rack schedule
POWER
A/B + generator
COOLING
One-unit-down heat path
CONTROL
Alarm and transfer rules
SITE
Capacity and residual risk
Notes: Chapter 18 closes with integrated design. The student deliverable should reconcile one set of future IT numbers across electrical and mechanical sheets, identify assumptions, and state the exact failure boundary rather than claiming an unsupported Tier. Citations: - Keentel Engineering, Data Center Design Guide, https://keentelengineering.com/data-center-design-guide